## Slide 1: Radioactive release during severe accidents at NPP with VVER reactors
SPAEP, 09.2007
Presented by Andrey Frolov, head of bureau of radiation protection

## Slide 2
Aim of analysis:
to identify the most important factors influencing the accidental releases magnitude
to estimate the main uncertainties and conservatism rate of design calculations
to show the way to correct design calculations by best estimate models
to show the importance of tasks investigating in Project
to find the experiment parameters for Task 2, 4, 6
Review of the design approaches was executed for:
“NPP-91” project with VVER-1000
EUR, NRC and IAEA recommendations for LWR NPP

## Slide 3
Point estimate diagram showing accidental releases of reference nuclides for various states of protective barriers/localizing systems
NPP-91 with VVER-1000

## Slide 4
Fractions of radionuclide retention in coolant system for PWR reactors (EUR recommendation)
FP group | Low-pressure scenario | High-pressure scenario
Xe | 0.0 | 0.0
I, Cs | 0.15 | 0.70
Te | 0.20 | 0.50
others | 0.20 | 0.50

## Slide 5: Large LOCA with black-out
Behavior of I-131, Cs-137, Sr-90, Te-131m, La-140 and Ru-103 in containment atmosphere at various stages of reference accident

## Slide 6: Large LOCA with black-out
Release of various forms of I-131 and other fission products during the first day of accident (containment leak)

## Slide 7: Contribution of main fission products to total activity (VVER)
Element | Mass, % | Activity, Тdecay = 0 day, % | Activity, Тdecay = 30 days, %
Xe | 0.44 | 3.9 | 0.4
I | 0.02 | 5.2 | 0.7
Cs | 0.2 | 3.5 | 1.3
Ru | 0.19 | 1.7 | 9.7
Sr | 0.07 | 4.2 | 6.7
Mo | 0.27 | 3.9 | 0.01
Ba | 0.14 | 4.4 | 2.9
Ce | 0.23 | 3.3 | 15.3
La | 0.1 | 4.8 | 0.0
total | 1.7 | 35 | 37

## Slide 8: FP release inside containment at various phases of accident

## Slide 9: Large LOCA with black-out
the magnitude of accidental release is proportioned to concentration of FP in containment atmosphere
concentration of volatile iodine reduce 10-100 time due to maintaining pH >7 during all stages of accident and 3-10 time by sorption at polymer facing, steel corrosion products and the core catcher materials
correct simulation of aerosol behaviour is necessary with taking into account the aerosol diameter distribution in dependence on time

## Slide 10: Main sources of uncertainties of accidental release estimates L – low, M – medium, H- high level
Group of phenomena | Uncertainty | Sensitivity | Note
Accumulation of FP in fuel | L | M | Calculation of fission products accumulation is performed according to the well verified methodic
Release of FP from fuel under heating and melting | L-M | M-H | Uncertainty for fuel model of VVER is related with evaluation of release of Ru forms and effects of fuel oxidation on fission products release.
Aerosol transport and retention in the primary circuit | M-H | M-H | For analysis of severe accident consequences with containment bypass related with significant releases.
Release of low volatile FP from molten pools (in-vessel) | H | M | Uncertainty for fuel model of VVER is related with evaluation of release of Ru forms and effects of fuel oxidation on fission products release. Conservative assumptions were used in the design calculations.
Release of low volatile FP from molten pools at the ex-vessel stage | M | L | A core catcher preventing core-concrete interaction and decreasing aerosol release at ex-vessel stage.
Aerosol behaviour in the containment | M | M-H | Design calculations are taking account only Brownian and gravity coagulation and gravitation sedimentation.
Iodine chemistry | L-H | M-H | level of uncertainty is connected with pH maintaining in containment. High sensitivity of results to parameters determining release of organic iodine forms. Conservative assumptions were used in the design calculations.
Release routs and failure mode effects | M | H | Sensitivity level is related to parameters determining leak rate and mode of containment leakage

## Slide 11
Conclusion
The analysis was shown the following main factors influencing the calculation accidental releases magnitude :
appreciably uncertainties at assessment of FP release from fuel for the elements referred to Ru group (Ru, Mo, Tc)
aerosol deposition and resuspension in coolant system equipments at primary-to-secondary leaks accidents (retention fraction up to 0,7)
iodine sorption at polymer facing, steel corrosion products and the core catcher materials (retention fraction up to 0,9)
correct calculating simulation of aerosol transport at containment and inter-containment space