## Slide 1
Simulation of LAVA behavior (#2916 CHESS)
RRC “KI”

## Slide 2: Simulation approach
Data on the geometry of compartments
Results of visual observations
Results of LFCM samples examinations
  Content of different species
  Properties measurements (density, viscosity)
Results of LFCM location (bore holes)

## Slide 3: Data uncertainties
Materials remained in the reactor and dropped into the reactor wreck (total of 16600 tons)
Start of melting and interactions with structural materials
Amount of materials incorporated into LFCM
Temperatures and properties

## Slide 4: Reactor materials

## Slide 5: Models used for analysis: Pancake model
Basemate concrete
Under reactor structures (Steel, sand)
“OR” Scheme (steel, serpentine)
Fuel containing masses (zirconium, steel, graphite, etc.)
Materials from upper structures (concrete, materials dropped into the reactor wreck)
Goal: Timing of events

## Slide 6: Computational model

## Slide 7: Calculated analysis
Main uncertainties:
  Boundary conditions
  Debris cooling by air
  Graphite burning
Calculated scenarios (Time of graphite burning: 4 days, 7 days, 10 days

## Slide 8: Conditions: 10 days after accident
The conclusion was that final state was reached in 12 – 15
days after accident

## Slide 9: Model of MCCI and long term behavior of LFCM
The objective was to analyze the following processes:
  LFCM cooling rates to assess characteristic times
  Concrete erosion depth in different rooms
  Concrete decomposition depth
Criteria of success
  Correspondence to observations
  Assessment of spreading times

## Slide 10: Initial data and results
Calculated temperature of the concrete under 305/2 was about 450K

## Slide 11: Results of calculations (4%)
Characteristic upper boundary cooling time about 5 hr
Characteristic LFCM cooling time about 20 hr

## Slide 12: Spreading model: Parametric study
Goals of use:
  Numerical predictions of spreading velocity
  Characteristic time of spreading
  Length of spreading
Temperature stopping criteria: cooling below 1100 K (viscosity exceeds 107 Pas)

## Slide 13: Spreading model: Parametric study

## Slide 14: Results of analysis
Spreading time is much shorter then cooling time if temperature exceeds 1100oC
Most probable temperature at the start of spreading was between 1000 and 1100oC

## Slide 15: Location of LFCM in the room 305/2

## Slide 16: Start of spreading
Intact thickness of wall between 305/2 and 304/3 was 0.93 m
Axial concrete erosion was about 0.7 m
Radial concrete erosion of the same order
Location of areas with high fuel content near the wall between 305/2 and 304/3
Wall crack
Elevations of FCM:
Room 305/2: about 11.0 m
Room 304/3: about 10.3 m

## Slide 17: Simulation of LFCM spreading
Initial data:
  3D geometry of rooms
  Varied temperature
  Assume two layers: black ceramics atop
Model includes
  Advection of the melt
  Radiation from melt top surface
  Heat conductivity
  Temperature dependence of viscosity
  Melt source (room 305/2) and melt sinks (room 301/6)

## Slide 18: Characteristics of horizontal flow

## Slide 19: Initial geometry
Room 305: Melt source
Initial height of melt in room 305: 1.7 m
Through wall break between 305 and 304 rooms (0.5 m)
Doors 1 m
305/2
304/3
303/3
302/3
301/5
301/6

## Slide 20: Initial data
Mass source: 20 kg/s
Melt temperature:, 1430, 1450 K
  1380 K, spreading length about 18 m
  1430 K, spreading length about 25 m
  1450 K, spreading length about 30 m
Qualitatively spreading length is predicted

## Slide 21: Uncertainties
The mass source in the room 305/2
Initial temperature
Dependence of viscosity upon temperature
Mass sinks to lower levels

## Slide 22: Summary
Models developed allowed assessments of significant phenomena during late phase of accident and timing of events
No significant interactions with concrete were predicted in the rooms 304/3, 301/5 and 303/3
Qualitative modeling of the spreading if temperature was about 1400 – 1450 K
Temperature dependence of viscosity needs some refinement

## Slide 23: Geometry of 305/2
Floor level 9.7 m
Cross basemate level 11.0 m
Steam valves elevation 0.4 m

## Slide 24: Section K+2400